7762AA Electrical Distribution (1)

Module Teacher-- U Kyaw Naing (Joe)             Delivery mode=  4 hrs per weeks x 9 weeks= 36 Hrs

# Main text book recommended for 7762AA Electrical Distribution

2832P Distribution and Utilization A

( Published by Department of Technical and Further Education-NSW)

| Unit | Contents | Module/ Learning Outcomes |
| --- | --- | --- |
| Unit 1 of 2832P | Design concept, character of plant, size and character of load, type of power supply to load, service requirement + 7762AA Module book | 7762-AA Learning outcome 1 |
| Unit 2 of 2832P | Transmission line construction Mechanical properties, overhead lines conductors, damper, fitting, insulator, OH line construction and maintenance regulations, sag etc +7762AA Module book | 7762AA Learning outcome 2 + Some components of Learning outcome 3 |
| Unit 3 of 2832P | Voltage regulation, control, transformer impedance+7762AA Module book | 7762-AA Learning outcome 4 |

Australian Standards-

AS 1026, 1023, 1034, 1042, 1078,1117,1158,1190,1202,1220,1222,1243,1284,1359, 1360,1469,1531,1675,1680,1746,1767,1768,1798,1824,1883,1930,1931,2005,2006,2184,2209,2263,2264,2326,2374,2421,3000,3116,3274

# Other text books

| Text book | Learning Outcomes of 7762AA Module |
| --- | --- |
| Generation, Transmission and Utilization of Electrical Power By AT Starr | Supporting reference |
| Basic Training Manual 16-12 Electrical Trades-Cable, conduits, busbar | Some components of Learning outcome 3 |
| Electrical Distribution Engineering | Support for Learning outcome 1,3 |
| Electrical Power Distribution & Transmission | Support for Learning outcome 2, |
| Electrical Power Transmission System-By R Robert Eata, Edward Cohen | Support for Learning outcome 1,2, |
| Site Surveying & Levelling By John Clancy + Internet downloaded article-Software package for line route survey + Transmission line mechanical design (Electrical Power Transmission System) | Survey for transmission line construction site and route + contour map of Learning outcome 2 especially for Line Design Project |

Day (1)

# Learning Outcome 1.1 Describe common system for electrical distribution

The electrical distribution system contains the following equipments.

- Power generating equipments

- Primary and secondary distribution systems including feeders, transformers, switch gears, protective equipments and stand by generating plant.

- Motor drives, heaters, oven, associated wiring and control equipments

- Lighting equipments, lighting wiring circuits

- Electrical and electronic control, instrumentation systems

- \Auxiliary systems

- Special items such as welding, batteries, rectifiers, electro plating equipments, lifts, industrial trucks, air-conditioners

- Communication equipments

- Yard, roadway, protective lighting

## Limit of Distribution

Figure 1.1

## System of distribution

- Overhead distribution

- Underground distribution

- Combined overhead and underground distribution

Learning outcome 1.2 State their relative merit and voltage levels

Overhead lines

- Less expensive

- Extreme higher voltage

- Continual stresses

- Exposure to varying climate conditions

- Subject to mechanical wears/ corrosion

- Need to be periodically replaced

Higher spacing between conductors---- Higher current rating

----- Higher circuit inductance

Larger conductor sizes----- Higher load capacity

------ Higher expenses

### Standard distribution voltages  ASCI 1969

Standard voltages for 3 phase system are

415V (Voltage to neutral  240V)

11KV, 22KV, 33KV, 66KV

Learning outcome 1.3 Interpret the diagrams of distribution systems

Fig 1.2

### Types of feeders

#### Radial feeder

Fig 1.3

#### Parallel Feeder

Fig 1.4

#### Ring main feeder

Fig 1.5

#### Substation busbar arrangement

For easy maintenance, means must be provided for isolators and circuit breakers. Earthing switch is to be provided for earthing of high voltage equipments.

#### Single busbar

Fig 1.6

#### Duplicate busbar

Fig 1.7

#### Sectionalize busbar system

Fig 1.8

#### Ring busbar

Fig 1.9

### Learning outcome 1.4 Recall terminating pertaining the distribution system

Technical terms for electrical distribution

#### Reserve

Reserve is that portion of an electric utility’s available generating capacity tahat is not producing electricity at a given time.

#### Spinning reserve

The generating capacity that is being driven at the proper speed to provide proper voltage but is not producing power. Spinning reserve can provide power to the system almost instantaneously if the system load is increased or a generator must be taken out of service.

Diversity

Load changes during a period of time.

Fig 1.10

Demand Factor

Maximum load

Demand factor =  --------------------------------------------------

Total connected load

Consumer Factor

An individual consumer is not opt to be using all of the electrical devices that constitute his or her connected load at the same time.

Maximum demand

Actual load is used by consumer creates demand for electrical energy that varies from hour to hour over a period of time but reaches its greatest value of same point. This may be called the consumer’s instantaneous demand.

Coincidence factor

The ratio of the maximum coincident total demand of a group of consumers to the sum of the maximum demands of each of the consumer

Maximum coincident total demand of a group of consumers

Coincidence factor = ----------------------------------------------------------------------------------------

Sum of maximum demands of each of consumers

Utilization factor

The ratio of the maximum demand of a system to the rated capacity of the system.

Maximum demand of the system

Utilization factor = -----------------------------------------------------------------------------------

Rated capacity of the system

Diversity Factor

The ratio of the sum of maximum demands of each of the component loads to the maximum demand of the load as a whole.

Sum of maximum demands of each of the component load

Diversity Factor = ---------------------------------------------------------------------------------------------

Maximum demand of the load as whole

Some natures  of industrial loads

Industrial Heating

Space heater, oven baking, heat treating, enamelling, furnace, steel brass, welders, high frequency heating devices.

Electric furnances draw the heavy current of less intermittently during the part of the heat treatment process and fairly lesser current for the rest.

Electronic loads

Radio, TV, Laser equipments, digital time and timing devices, rectifiers, oscillators, high frequency current production.

TUTORIAL EXERCISES

Q1.

Discuss the relative advantages and disadvantages of the following systems of electrical distribution.

- radial feeder  (b) Parallel feeder  (c) Ring main feeder

Answer will be discussed in the class.

Q2.

A transformer supplies a group pf four feeders which have individual maximum demands of 2.5, 2.4, 4.3 and 1.6 MVA. If the diversity factor of the system is 1.82, determine the maximum demand on the transformer.

Answer

Sum of the individual maximum demands

Diversity Factor  = ------------------------------------------------------------------------------------

Maximum demand of the transformer.

2.5 + 2.4 + 4.3 + 1.6

1.82    = -----------------------------------------------------------------------------------

Maximum demand of the transformer.

2.5 + 2.4 + 4.3 + 1.6

Maximum demand of the transformer = ---------------------------------------------------

1.82

Maximum demand of the transformer= 5.93 MVA

Q3

A house has the following loads

5 lights each 80watts

1 stove  1000watts

5 power points   each 100 watts

1 air-conditioner    1000 watts

If maximum demand is 2000 watt, calculate the demand factor.

Total connected load

| Equipment |  | Power |
| --- | --- | --- |
| Light | 5 x 80 watts | 400 watts |
| Stove |  | 1000 watts |
| Power point | 5 x 100 watts | 500 watts |
| Air-conditioner |  | 1000 Watts |
|  | Total connected load | 2900 watts |

Maximum demand

Demand factor = ----------------------------------------------------

Total connected load

2000

= -----------------------------------------

2900

= 0.68

### Q4

State 3 classifications of distribution system

Answer

- Overhead distribution

- Underground distribution

- Combined overhead and underground distribution

### Q5

State the standard voltages for 3 phase distribution system

Answer

415V, 11KV, 22KV, 33KV, 66KV

### Q6

Sketch abd describe a single wire earth return (SWER) system

Fig 1.11

### Q7

Sketch three types of feeders that are commonly used for distribution system and describe the merit of each type

Answer

Radial feeder

Fig 1.12

Advantage-- Simple to build and maintain

Disadvantage-- Unreliable

Parallel Feeder

Fig 1.13

Advantage-- Reliability is improved over radial feeder

Disadvantage- Expensive and more complex to operate

Ring main feeder

Fig 1.14

Advantage-- Very reliable due to multiple sources and two ways of power flow

Disadvantage-- Very expensive and complicated to operate

### Q8

Draw a block diagram of a power system from generation to utilisation and on it, show typical voltages

Answer

Fig 1.15

Q9

Sketch the following busbar arrangements

-Single busbar

-Sectionalise busbar

-Ring busbar

-Duplicate Busbar

Answer

Single busbar

Fig 1.16

Sectionalise busbar

Fig 1.17

Ring busbar

Fig 1.18

Duplicate busbar

Fig 1.19