7762 AA Electrical Distribution (1)

Day 2

# Learning outcome 2.1 Identify relevant components used in overhead line design

Conductor support

Wood poles

Steel poles

Concrete poles

Steel Towers

## Typical Pole

Fig 2,1

Fig 2.2

Fig 2.3

Fig 2.4

More angle of deviation causes the bigger resultant force to remove the cable from the pin insulator. The angle of deviation should not be more than 10 degree for pin insulator.

Fig 2.5

### Arcing Horns

In the case of insulator flash over due to lightning strike, the porcelain is often cracked  or broken by the power arc that follows the initial discharge.

To protect against this trouble, arcing horn or rings are installed on many overhead systems. These operate so that the arc is taken up by the electrode and held at sufficient distance from the porcelain to prevent the damage by the heat of the arc.

Fig 2.6

Fig 2.7

Fig 2.8

These consist of a number of helically formed rods , the  central portions of which are shaped to provide attachment of the conductor on line pin insulator.

Outcome 2.2 Outline relevant factors related to installation, maintenance of cross arms, pole types and choice of conductor sizes for commonly used configuration.

## Conductor size

SAA Wiring Rule

## Rule 3.13.2

Every conductor installed as aerial conductor shall have not less than seven strands and shall not be smaller than 4 mm2 copper or 16mm2 aluminium.

Fig 2.9

Total CSA  = 4 mm2 copper or 16mm2 aluminium

## The length of span of aerial conductor

Fig 2.10

## Rule 3.13.9

The length of span of copper aerial conductor shall not exceed the values given below,

| Type of conductor | Size mm2 | Maximum span (metres) |
| --- | --- | --- |
| Bare hard drawn conductors | 4 6 16 or over | 25 30 60 |

#### Learning outcome 2.3 Determine mechanical limitations and physical dimensions of lines

## Overhead line conductors

- Hard Drawn Copper Conductor

- All Aluminium Conductor (AAC)

- All Aluminium Alloy Conductor (AAAC)

- Aluminium Conductor Steel Reinforced (ACSR)

- Steel Conductor Galvanized (SC/GZ)

- Steel Conductor Aluminium Clad (SC/AC)

When steel is used as reinforcement or as a conductor or stay, it must be protected against corrosion.

## Protection methods

- Galvanizing

- Coating with aluminium

## Note

(1)An aluminium conductor steel reinforced should have some indication of the corrosion prevention method.

ACSR/GZ indicates that steel is galvanized

ACSR/AC indicates Aluminium Steel Core.

(2)Aluminium Conductors with Steel reinforcement provides the following advantages

- Most economical

- Shorter Span

- Not so frequently used for distribution work

## Steel Conductor

- Very economical for rural distribution

## Aluminium/ Aluminium Alloy Conductor

- Financial saving over copper

- Use in suburban work

- Span lengths are relatively short allowing for lower line tension

## Conductor current rating

The current rating of overhead conductor depends on

- Heating

- Voltage drop

- Power losses

The current carrying capacity of an overhead conductor is limited by

- Annealing temperature of conductor

- The expansion due to temperature rise which causes a reduction of statutory clearance

- A temperature rise which might occasion injury to any insulation

## Reasonably accepted values for the maximum operating temperature

75° C for continuous rating

100° C for one hour rating

## Conditions affecting maximum conductor temperature

- Ambient temperature

- Wind velocity

- Heat absorbed from solar radiation

- Heat lost by convection

- Heat lost by radiation

## Fault current carrying capacity

Fig 2.11

## Voltage

The conductor must operate so that when the maximum current is being conveyed the fall in voltage along the line is within the certain limit.

The consumer’s main to any point on the installation does not exceed five percent of the voltage at the commencement when full current is flowing

For medium voltages, the variation at the consumer’s terminals should not exceed six percent and for higher voltages, the variations should not exceed ten percent.

## Power loss

1

Power Loss             I 2               ------------------------------

Cross Sectional Area

Where Power loss means consumer power loss and line power loss.

Cross sectional area of the conductor determines the capital cost.

## Materials for over head line conductors

Materials for overhead line conductor is determined by

- Electrical properties such as resistance, reactance, current carrying capacity of the conductor

- Mechanical properties such as strength and weight

- Price of the material relation to the return in the investment

## Factors to be taken for installation of insulator

- Minimum mechanical strength

- Minimum impulse withstand voltage

- Minimum wet withstand voltage at power frequency

- Minimum puncture voltage at power frequency

- Minimum creepage distance between conductor tie and pin

The minimum failing load for any line pin insulator is 7KN.

## Designation of insulator

Line Pin Insulator

| First letter | S- Standard F-Foy type A-Aerodynamic |
| --- | --- |
| Next letter | LP- Line pin insulator First number- Nominal voltage (KV) Second number- Minimum creepage distance |

## Example

ALP  33/920

A- Aerodynamic type

LP- Line pin insulator

33- 33 KV

920- 920mm (Minimum) creepage distance

## Example

SLP  11/180

S-Standard type

LP-Line pin insulator

11-11KV

180- 180 mm (Minimum) creepage distance

## Shackle Insulator

Shackle insulators are used for terminating and angle construction on mainly on low voltage lines. The high voltage shackle insulators are now replaced by disc insulator.

Fig 2.12

SH LV1- Minimum failing load 9KN

SH LV2- Minimum failing load 20KN

## Disc Insulator

Disc insulators are used in high voltage lines for both intermediate and strain construction

1 disc- 11KV

2 disc- 22KV

3 disc- 33KV

Minimum failing loads  of 44 KN and 66 KN

S-Suspension              A- Anchor shackle    B- Hanger bracket     D- Disc    E- Eye bolt      N- Eye nut

P1-Pole band termination    P2- Pole band through construction   G- Straight torque

## Example

EA 2/D

E- Eye bolt

A- Anchor shackle

2-2 discs

D- Disc

## Stay Insulator

| Stay insulator type | Line voltage | Steel wire size | Minimum failing load (KN) |
| --- | --- | --- | --- |
| GY1 GY2 GY3 GY4 | LV and 11KV 11KV 22KV 33KV | 7/2.75 19/2.00 19/2.75 19/2.75 | 27 71 222 222 |

## Insulator pin

- Made of hot rolled carbon steel and galvanized

- Alloy lead -- 95% lead and 5% antimony

- Pattern A, B ,C

- A- Used for both medium and high voltage insulators

- B-Used for insulator of voltage up to 600V

- C- Used for high voltage insulator

Interpretation

Type/ Stem length / Failing load

| Pin Type | Shank Size |
| --- | --- |
| B / 100 / 3.5 A / 130 / 7 C / 150 / 7 C / 150 / 11 C / 200 / 11 B / 300 / 7 | 140 x 16 mm 165 x 20 mm 165 x 20 mm 165 x 24 mm 165 x 24 mm 165 x 24 mm |

## Example

C / 300  / 7

C Type    Stem length 300 mm  Transversed failing load 7 KN.

## Causes of insulator failure

- Cracking of porcelain

- Porosity of porcelain

- Puncture of weak porcelain

- Shattering of insulatoir caused by power arc

- Flash over of insulator caused by dust/ salt deposits

- Failure of insulator from excessive mechanical stress

- Short circuit caused by birds or animals

## Maximum tension of conductor

Maximum tension should not be more than 50% of ultimate tensile strength under a wind loading of 500 Pascal at 15 º C

The maximum conductor tension in still air at 5 º C is not to exceed the followings

15%- Ultimate Strength for hard drawn copper conductor

18% Ultimate Strength for hard drawn all aluminium  conductor, steel core aluminium conductor and hard drawn cadium copper conductor

18% Ultimate Strength for all aluminium alloy conductors

## Vibration dampers

33 1/3 % for hard drawn copper conductor

25%  for hard drawn aluminium steel core and hard drawn cadium copper conductor.

Vibration dampers are fitted to transmission lines rather than distribution feeders

## Armour rod and vibration dampers

Over head line conductors are subject to mechanical vibration caused by change of wind pressure causing swing and ultimately causing failure of the conductor.

Such failure is reduced greatly where conductor is reinforced at the point of support and by designed conductor clamp.

## Helically formed fittings

Fig 2.13

Helically formed fitting is applied to a conductor at the support point.

## Line Guard

Features:

- Shorter in length

- Smaller diameter wire

- Used at conductor support

- To protect the conductor against flash over burn

## Termination or dead ends

- Helically formed wires

- Leaving loop to which tension is applied

## Insulation material for conductor

Polyvinyl Chloride (PVC)

- Low temperature, tearability, oil resistance, termite resistance

- Fuse / protective devices must be sufficiently sensitive to prevent PVC approaching softening point.

Ethylene Propylene Rubber (EPR)

- Thermosetting, excellent thermal electrical properties

- Higher dielectric , greater resistance to corona

### Impregnated Paper

- Must be free from inperfection , High dielectric strength

Cross Linked Polyehylene (XLPE)

- Used for power cables

- Extremely good chemical resistant insulation

- Short time operation at 130 º C

- Continuous operation at 90 º C

- Short circuit performance at 250 º C

- Lightness

### Compacted conductors

- Used for 1.9/ 3.3 KV cables

- HV XLPE cables are compacted to reduce the size of intersticies.

### Overhead line consideration

AC transmission is mostly used. Overhead line construction are much less expensive than under ground line construction.. Steel towers are used to support the conductors. They are protected by lightning arresters.

## Cable

Majority of cable used for underground distribution work are Impregnated Paper  insulated with lead or lead alloy sheath. Cables up to 33KV are covered by AS 1026. Copper and aluminium are used as conductors.

#### Learning Outcome 2.2 Outline relevant factors related to installation

## Ultimate Tensile Strength

Fig 2.14

The following regulations are extracted from Overhead Line Construction Regulations of NSW (1983)

## Regulation 28.1

The ultimate tensile strength of an aerial conductor operating voltage of 650V or less shall not be less than 3000N.

Hard Drawn Copper  Conductor      7/1.75 at 3610 N Ultimate Strength  (UTS)

All Aluminium Conductor                 7/1.75 at 3010 N  Ultimate Strength  (UTS)

All Aluminium Alloy Conductor        7/1.75 at 4710 N  Ultimate Strength  (UTS)

## Regulation 28.2

The Ultimate Tensile Strength of an aerial conductor operating voltage exceeding 650V must not be less than 5000N.

Copper                   7/1.75    at   6840 N Ultimate Strength

Aluminium             7/2.50     at   5750 N Ultimate Strength

Aluminium Alloy    7/2/25     at   7780 N Ultimate Strength

#### Learning Outcome 2.3 Determine Mechanical & Physical dimension of line

## Sag

Fig 2.15

When distribution lines are erected, the sag allowed in a conductor at the time of erection must be such that the maximum tension allowable for the particular conductor is not exceeded under the condition specified in the regulations.

## Four sag conditions

- Sag and tension in conductor at 15ºC with wind loading of 500 Pascal on the projected area of conductor

- Sag and tension at no wind and ambient  temperature of 5ºC .

- Sag at 5ºC which determines the support weight to maintain the statutory clearance above the ground.

- Sag of erection which will ensure that the above conditions are fulfilled.

Fig 2.16

W  L 2

S =  -----------------------------

8 T

Where

| S L W T | = Sag in metres = Length of span in metres = Combined load of gravitational force and wind force on conductor at one metre length = Tension in conductor (Newton) |
| --- | --- |

8 x  S 2

Length of  cable (Metre)  =   L +  -------------------------------

- x L

## Problem

Calculate allowable sag for a 7/ 3.50 hard drawn copper over head line conductor span of 150 m. The wind loading is 500 Pascal. Minimum tension is 50% of Ultimate Strength.

| Ultimate tensile strength Gravitational force Diameter of conductor Wind loading per metre Combined load of gravitational force and wind force on conductor at one metre length W L 2 7. 934 x 150 2 Sag = ------------------------- = ----------------------------- 8 T 8 x 26600 x 0.5 | = 26600N = 5.949N / m =10.5 mm =diameter in metre x wind loading in Pascal = 10.5 x 10 - 3 x500 = 5.25 N/ m = Wo 2 + W l 2 = 5.949 2 + 5.25 2 = 7.934 N/ m = 1.678 m |
| --- | --- |

### Erection Sag

It is necessary to calculate the tension and  sag under conditions at the time of erection.

### Factors to vary sag and tension

- Elasticity

- Temperature

An increase in temperature will cause the length of the conductor to increase so that the sag will increase.

### Sag measurement

(a) Sight Board Method

Fig 2.16

Sag= h 1 - h 2

Sight boards are fixed to two poles of the span at the appropriate height for desired sag. The conductor is then pulled up to line with a sight taken between two boards.

(b) Wave Timing Method

Fig 2.17

For this method, the conductor is struck at one end of the span and the time taken for the wave to travel the span six times is measured. Sag is then calculated from the formula.

t  =         Sag in metre

t= Time in seconds for 3 return waves

(c) Optical Range Finder Method

Fig 2.18

Sag= h 1 - h 2

Measure the height of the conductor at the pole . The height of the conductor at mid span.

Sag= Height of conductors at pole  = Height of conductor at mid span

Wood poles

- Cheapest

- Made from larch, sprace, cedar, pine, fir trees

- Southern Yellow Pine , Dogulas Pine are mostly used.

## Review Questions

Review Questions are extracted from EA 153 - 7762 AA Electrical Distribution Module Book

Review Questions for Section 2-Over Head Line

Answers for Q1 to 4

Answers for Q5 to 10

Answers for Question 11 to 20

Answer for Question 21 to 23